## 10BP
BP scores (Percentile) |  | 35.3333 |  | 10 BP Energy efficiency expert evaluation form | [12 empty] | guide
1 | Measurement and management | Data Management | Energy and Process Control |  |  |  | steam |  | natural gas |  | water |  | Electricity |  | Fuels (coal, heavy oil) | Remark
|  | None (0); | No (0) |  |  |  | Level 1 measurement, metering whole plant consumption (0) |  | Level 1 measurement, metering whole plant consumption (0) |  | Level 1 measurement, metering whole plant consumption (0) |  | Level 1 measurement, metering whole plant consumption (0) |  | Level 1 measurement, metering whole plant consumption (0) | Basic data management is being done. Electricity generation data is logged and live. Other data manually entered. | 1, data management score, the ability of enterprises need to be asked and actual examples of certification such as daily record companies say there should be random view and take photos.
|  | There are daily recording and analysis (+1) | the water volume and temperature in the resin and dyeing process is set and controled by operators (+1) |  |  |  | Level 2 measurement, metering every workshop consumption (1) |  | Level 2 measurement, metering every workshop consumption (1) |  | Level 2 measurement, metering every workshop consumption (1) |  | Level 2 measurement, metering every workshop consumption (1) |  | Level 2 measurement, metering every workshop consumption (1) |  | 2, scoring three measures, not all devices are installed metering considered three measures. Businesses of their key energy metering equipment, and two measures of up to 100% is considered to achieve the three measures. And it should be noted that the meter is accurate or not,
|  | energy and water consumption indicators are developed (+1) | the water volume and temperature in the resin and dyeing process is set and automaticly controled (+2) |  |  |  | Level 3 measurement, metering the key equipements(3) |  | Level 3 measurement, metering the key equipements(2) |  | Level 3 measurement, metering the key equipements(2) |  | Level 3 measurement, metering the key equipements(2) |  | Level 3 measurement, metering the key equipements(2)
|  | A central monitoring system is installed (1) | Installation humidity control system in drying process (+1) |  |  |  | flow chart of steam system (1) |  | flow chart of natural gas systems (1) |  | flow chart of water system (+1) |  | flow chart of electrical system (1) |  | Fuel consumption analysis chart (+1) |  | 3, energy and process control, should be on-site to see if there are installation, installation and operation are reasonable.
|  |  | The equipment initial water input is controled and monitered (+1) |  |  |  | Chart of steam measurement network (1) |  | chart of gas measurement network (1) |  | Chart of water measurement network (1) |  | Power compensation (+1) |  | Fuel output efficiency analysis chart (+1)
|  |  | Energy centralized control system and enterprise resource planning (ERP) system combined (+1) |  |  |  | Steam balance data reporting and analysis (+1) |  | Natural gas balance data reporting and analysis (+1) |  | Water balance data reporting and analysis (+1) |  | Or more than 20kw motor efficiency motors are inverter (+1)
|  |  | Rationalize production schedule, and reasonable exchange devices (cylinders, vats, tanks etc) washing(+1) |  |  |  | Steam consumption analysis chart (+1) |  | Gas consumption analysis chart (+1) |  | Water consumption analysis chart (+1)
[7 empty] | Steam output efficiency analysis chart (+1) |  | Gas output efficiency analysis chart (+1) |  | Water production efficiency analysis chart (+1)
Score | 19 | 1 | 3.5 |  |  |  | 3 |  | 2.5 |  | 1 |  | 5 |  | 3
All Scores | 40 | 3 | 6 |  |  |  | 8 |  | 7 |  | 7 |  | 5 |  | 4
2 | Condensate water collection and recycling | Condensate Recovery |  | Energy recovery performance | [7 empty] | Insulation and sealing system |  |  |  | Remark
|  | No (0) |  | The establishment of condensation water reuse analysis reports and records (+1) | [7 empty] | No (0) |  |  |  | Condensate recovery is very low due to contamination in condensate from leaking heat exchangers in dyeing machines. | 1, the first data recovery based on measurement data
|  | <20% (1) |  | Metering the condensate water reuse (1) | [7 empty] | Condensate pipe insulation (1) |  |  |  |  | 2, metering imperfect, need to be estimated according to the situation, the main condensate discharge point estimates. Remarks should describe the basis for judgment
|  | 20% - 40% (2) |  | Condensate overflow discharge rate of 0-5% (3) | [7 empty] | Condensate collecting tank insulation (1) |  |  |  |  | 3,
|  | 40% - 60% (3) |  | Condensate overflow discharge rate of 5-10% (2) | [7 empty] | Closed condensate recovery system, no flash steam (+2)
|  | 60% --80% (4) |  | Condensate overflow discharge rate of 10-20% (1) | [7 empty] | Open-celled condensate recovery tank, a small amount of flash steam (+1)
|  | > 80% (5) |  | Condensate overflow discharge rate <20% (0)
Score | 2 | 1 |  | 0 | [7 empty] | 1
All Scores | 15 | 5 |  | 5 | [7 empty] | 5
3 | Cooling water reuse efficiency and | Cooling water recovery |  | Energy recovery performance | [11 empty] | Remark
|  | None (0) |  | Establish cooling water reuse analysis reports and records (+1) | [7 empty] | No (0) |  |  |  | Significant potential in cooling water recovery. | 1, the first data recovery based on measurement data
|  | <40% (1) |  | Metering the cooling water reuse (1) | [7 empty] | Cooling water pipe insulation (+0.5) |  |  |  |  | 2, metering imperfect, need to be estimated according to the situation, the main condensate discharge point estimates. Remarks should describe the basis for judgment
|  | 40% - 60% (2) |  | Overflow discharge of cooling water 0-5% (3) | [7 empty] | A cooling water heat sump (+0.5)
|  | 60% --80% (3) |  | Overflow discharge of cooling water 5-10% (2)
|  | 80% --100% (4) |  | Overflow discharge of cooling water 10-20% (1)
Score | 1.5 | 1 |  | 0 | [7 empty] | 0.5
All Scores | 10 | 4 |  | 5 | [7 empty] | 1
4 | Process water and wastewater reuse efficiency | Efficiency process water | [6 empty] | Energy recovery performance | [6 empty] | Remark
|  | Efficient washing process and equipments (2) | [13 empty] | Condensate and other process water are discharged. | 1, the recovery rate, temperature data based on first measurement data
|  | Efficient dyeing process and equipments (2) | [6 empty] | The temperature difference of reusing and collecting the process water is between 10 deg.] C and 20 ℃ (1) | [7 empty] | 2, metering imperfect, need to be estimated according to the situation, the main condensate discharge point estimates. Remarks should describe the basis for judgment
|  | Recycling rate: None (0); <5% (1); 5% --10% (2); 10% --20% (3); 20% --30% (4); 30% -50% (5 )> 50% (6) | [6 empty] | The temperature difference of reusing and collecting the process water is less than 10 ℃ (2)
Score | 3 | 3 | [6 empty] | 0
All Scores | 12 | 10 | [6 empty] | 2
5 | Discharged Hot water heat recovery | Thermal waste heat recovery |  |  |  |  | Energy recovery performance |  |  |  | Insulation System |  |  |  |  | Remark
|  | None (0); <20% (1); 20% - 40% (2); 40% - 60% (3); 60% --80% (4) |  |  |  |  | The final waste water discharge temperature is greater than 40 ℃ (1) |  |  |  | No (0) |  |  |  |  | No wastewater heat recovery system installed. Need to separate the hot and cold water discharge lines. | 1, the recovery rate, temperature data based on first measurement data
|  | > 80% (5) |  |  |  |  | Final effluent discharge temperatures between 30 deg.] C and 40 ℃ (2) |  |  |  | Pipeline insulated(+1) | [5 empty] | 2, metering imperfect, need to be estimated according to the situation, the main condensate discharge point estimates. Remarks should describe the basis for judgment
[7 empty] | The final waste water temperature below 30 ℃ (3) |  |  |  | Tank / pool / water tank insulated (+1)
Score | 0 | 0 |  |  |  |  | 0 |  |  |  | 0
All Scores | 10 | 5 |  |  |  |  | 3 |  |  |  | 2
6 | Boiler efficiency improvement | Boiler efficiency (coal-fired) | [13 empty] | Remark | 1, first of all based on measurement data or test report
|  | <40% (0) 40-45% (1) 45-50% (2) 50-55% (3) 55-60% (4) 60-65% (5) 65-70% (6) 70 75% (7) 75-80% (8) 80-85% (9)> 85% (10) |  |  |  |  | Third-party agencies test boiler efficiency every 3 years and provide reports (1) Third-party agencies test boiler efficiency every 2 years and provide reports (3) Boiler efficiency is tested annually by third-party agencies and reports (5) |  |  |  | Boilers are heat, power and cool co-productiond (5) Boilers are heat and power cogenerationd (3) |  |  |  |  | Boilers are for steam generation mainly and equipped with heat recovery systems. Potential for improving efficiency exists. | 2, metering imperfect, need to be estimated according to the situation, the main condensate discharge point estimates. Remarks should describe the basis for judgment
Score | 11 | 6 |  |  |  |  | 5 |  |  |  | 0
All Scores | 20 | 10 |  |  |  |  | 5 |  |  |  | 5
7 | Steam traps and steam system performance | Trap Performance | [5 empty] | Flash steam and steam leakage management |  |  |  |  | Steam system efficiency |  |  | Remark
|  | The bypass valve remains open (0) | [10 empty] | steam transport in high pressure and utilized in low pressure(2) |  |  | Steam traps are by-passed mainly due to back pressure on traps. Condensate discharged due to contamination.
|  | Occasionally the bypass valve is opened, the trap performance is poor (1) | [5 empty] | No visible flash steam line or leakage of steam (1) |  |  |  |  | Steam piping layout is reasonable (2)
|  | The bypass valve has been closed, the poor performance of the trap (2) | [5 empty] | No internal leakage valve (1) |  |  |  |  | All of the heating process in indirect heating (+2)
|  | The bypass valve has been closed, the normal performance of the trap (3) | [10 empty] | Steam supply system had no significant imbalances (1)
all condensate water in drying cylinders are discharged (+1)
Hydrophobic along with the steam pipe (1)
Regularly check and record the traps(+1)
Score | 3.5 | 1 | [5 empty] | 0 |  |  |  |  | 2.5
All Scores | 15 | 6 | [5 empty] | 2 |  |  |  |  | 7
8 | Insulation Optimization | Valve insulation | [6 empty] | Piping and equipment insulation | [6 empty] | Remark
|  | No (0) | [6 empty] | No (0) | [6 empty] | Pipes are well insulated. Insulation of valves is proposed. | Insulation should be sampled statistics, business statistics and then ask
|  | Insulate the main pipeline valve (0.5) | [6 empty] | * Insulation main pipes (+1)
|  | 50% or more of the valves insulation (1) | [6 empty] | * Insulation of the branch pipes (+1)
|  | more than 60% of the thermal valves (1.5) | [6 empty] | insulate dyeing vat * (+1)
|  | More than 80% of the insulation valves (2) | [6 empty] | * Insulation of the washing machine (+0.5)
|  | insulate all valves (2.5) | [6 empty] | insulation of the drying cylinder * (+1)
Score | 3.5 | [7 empty] | 3.5
All Scores | 7 | 2.5 | [6 empty] | 4.5
9 | Setting machine efficiency optimization | Exhaust gas heat recovery |  |  | Whether to perform the humidity control | [5 empty] | Heating and piping insulation |  |  |  |  | Remark
|  | Recovery of less than 10% (1) |  |  | No (0) | [5 empty] | No (0) |  |  |  |  | Heat recovery is installed at 1 stenter and recommended on all remaining as well.
|  | Recycling of 10% -40% (2) |  |  | Infinitely variable setting machine by manual control of the exhaust fan (1) | [5 empty] | Exhaust channel is well insulated (1)
|  | Recycling of 40% -70% (3) |  |  | Automatic control exhuast air by an exhaust vent humidistat (+2) | [5 empty] | Heat exchange and the oven surface is well insulated (1)
|  | Recycling of 70% -90% (4) |  |  | cloth Humidity control before the setting machine (1) | [5 empty] | Regular cleaning of the oven heat exchange device (+1)
|  | Recycling of 90% -100% (5) |  |  | cloth humidity control after the setting machine (1) | [5 empty] | no pass by Heating or no wind pressure disorder (+1)
Implement all the measures mentioned above and runs well (+1)
Score | 5 | 1 |  |  | 1 | [5 empty] | 3
All Scores | 15 | 5 |  |  | 6 | [5 empty] | 4
10 | Compressed air system optimization | compressed air leak management |  |  |  | Compressed air pressure management |  |  |  | A continuously variable frequency/speed driver system (VSD) Control |  |  |  | Compressor room conditions |  | Remark
|  | No (0) |  |  |  | Pressure over a 7bar (0) |  |  |  | No (0) |  |  |  | cool (0.5) |  | VFD Installed on both compressors. Need to develop leakage management program. | Key parameters include: gas production, electricity, air pressure, etc. The main purpose
|  | Yes （1) |  |  |  | A pressure between 6 bar and 7 bar (1) |  |  |  | Yes（1) |  |  |  | dry (0.5)
|  | Set Leak indicators and check it at regular intervals(2) |  |  |  | A pressure lower than 6 bar (2)
Score | 4.5 | 0.5 |  |  |  | 2 |  |  |  | 1 |  |  |  | 1
All Scores | 6 | 2 |  |  |  | 2 |  |  |  | 1 |  |  |  | 1
Score | 53
All Scores | 150